GAUS BATTERY CHARGER 

GBC36V30A

High Frequency Intelligent Multi Step Charger

DESCRIPTION AND USER MANUAL

[image: image4.jpg]



Belgrade, July 2015.

1. TABLE OF CONTENTS

21. TABLE OF CONTENTS

2. GAUS BATTERY CHARGER GBC36V30A
3
TECHNICAL SPECIFICATIONS
4
4. LCD Display
5
4.1. Setting mode
5
4.2. Main screen (display)
5
4.3. The list of all the messages GBC36V30A is able to register while operating
6
5. INSTRUCTION FOR USE
8
5.1. Device installation
8
5.2. Starting charge
8
6.  DEVICE SETTINGS
9
7. LEGEND OF MARKS (SIGNS) AND CONCEPTS
12
Default settings for Gaus Battery Charger GBC36V30A
13
9. PRECAUTION MEASURES
14


2. GAUS BATTERY CHARGER GBC36V30A

· [image: image1.jpg]GBCABV30A

=
e
[}
==
=
=
e
>
as
i
E
=
==}
(7]
=
=%
=]




High frequency intelligent universal charger

· Constant voltage charging with current limit

· Maintenance operation (poofer connection with loads)

· Multi step charging (selectable different current and voltage limits…)

· For all types and technologies of starter, traction or stationary batteries

· Automatic start for typical battery

· More than 10 precautions measures including reverse polarity and power failure protection…

· High efficiency and power safe…

· LCD alpha-numeric display for current, voltage, Ah, stop-watch, messages, alarms (option)…

· Keyboard for more than 10 menus for setting of charging parameters (option)

· Desk or wall mountable (up and down)

GBC36V30A (GBC) is microprocessor device for charging and maintenance of all types lead-acid batteries (all nominal capacities and technologies) nominal voltage 36V. It is developed as a consequence of need for small, easy for use, safe, reliable and relatively cheep device for servicing and maintenance of starter and traction (industrial) batteries. GBC is mono phase high frequency half-bridge constant voltage charger with current limit. That means that current reaches output voltage on connected battery, which is limited. After reaching desired voltage, that voltage level is maintaining constant and charge current drops as battery is charging. Charge current (current limit) is selected as function of nominal battery capacity. Also, charging voltage is settable for different battery technologies. Voltage, current, duration and capacity are controlled and many precaution measures are implemented.

As device is microprocessor, with measuring current, voltage, duration, Ah, temperature of heat sink of semiconductor parts and power transformer, it is possible to implement different algorithms. It is possible to change voltage and current limits, conditioning of charge characteristic, pausing, waiting for event (measuring Ah during charge), conditioning end of charging (duration, Ah...) etc. 

[image: image2.jpg]GBCABV30A

=
e
[}
==
=
=
e
>
as
i
E
=
==}
(7]
=
=%
=]




Energy circuit is made of input filter with high quality electrolytic capacitors (EPCOS-SIEMENS 105C), high-frequency transformer (ETD Siemens) and mosfet half-bridge (International Rectifier IR), ultra fast diodes, inductance and PWM modulator. Working frequency is 50 kHz.  

Thanks to voltage limit, it is possible to charge without surveillance, because there is not over charge (over night or during weekend). As well, in a case of main power failure during charge, after it’s returning device automatically continues charging with parameters, which were previously set (before power failure). LCD display with 2x16 characters shows values of current, voltage, time, capacity, device status, warnings, alarms etc (option). There are more than 10 menus for setting the parameters of charging (option). Device is placed in red plasticified steel box with PVC distancers. Start (scroll) and stop (select) buttons, switches R/S (Ready/Set) and 48/36V, led diodes and LCD display for indication are placed on the devices front panel (option). Main switch, charge cables, power supply cable, fuse in DC circuit of charger, fuse in AC circuit and holders for cables are on the back panel of device. In version with automatic start without display and keyboard, led diodes on front panel indicates charger conditions (battery charging, constant voltage charging, charge finished and problem with battery).

Gaus Battery Charger GBC36V30A has following protections:

1. no sparks during connecting or disconnecting plugs from battery in charge operation;

2. forced temperature controlled air cooling;

3. control of a minimum of allowed connected battery voltage (forbidden start for voltages less than 5V);

4. temperature protection on heat-sink of semiconductor energy components;

5. [image: image3.jpg]GRUS BATTERY CHRRGER
GRCABV30N




in case of main power failure, after its restoring, charging automatically continues with earlier set parameters;

6. slow fuse T16A 30mm in AC circuit;

7. slow fuse T40A in DC circuit;

8. soft start of PWM modulator;

9. soft start in charging input electrolytic capacitance;

10. short circuit protection (if detected current is more than 32A charger is automatically turned off);

11. over voltage protection; 

12. protection from plugs (cables) falling during charge (freezing device until solving of problem);

13. Reverse polarity protection with forbidden start.

TECHNICAL SPECIFICATIONS

-Type of voltage converter: monophase half-bridge DC-DC converter;

-Supply 230V +/- 10%, 50Hz-60Hz 1.7kW; output power 1500W;

-Nominal input current:
8A; maximal start current:
10A

-Instruments:
LCD display 2x16 characters, ampermeter 0-40.00A, voltmeter 0-100.0V, temp1 

–99ºC do 99ºC or 4 LED diodes 

-Cables with Pb plugs: l=2m, S=6mm2

-Ambient temperature: 5 do +40ºC

	Charge current
	0-30A Cn/10, option: settable: 0.2-30A, step 1A (option step 0.1A)

	Battery type
	36V (6x6V); Cn from 33Ah to 300Ah, Sb-Sb, Sb-Ca, Ca-Ca, AGM, Gel

	Charge voltage range
	5-50V (permitted by software)

	Output voltage
	Option: settable: 2.20-2.75V/Cell x 6,12,18 Cells

	Capacity
	Charging 6x6V or 3x12V (18 cells in serial connection)

	Accuracy
	Better than 3%

	Resolution
	100mA and 100mV 

	current pulsation
	0,2A max

	output voltage pulsation
	<200mV

	Energy circuit
	MOSFET transistors, ultra fast diodes 

	Frequency
	50kHz

	Ŋ
	90%

	Cooling
	Temperature controlled forced air

	Control characteristic
	Constant voltage charger with current limit

	Control variable
	Current, voltage, capacity Ah, time

	LCD display during charge
	Status, current, voltage, duration, Ah, warnings, alarms…or 4 LED diodes

	Display
	LCD display with 2x16 characters or 4 LED diodes

	Control elements
	Main switch, start and stop buttons, switches Ready/Set and 48/36V (option), LED diodes

	Housing
	Steel red plasticified box RAL 3002 

	Dimensions (WxDxH)
	300x270x185mm

	Weight
	8kg


GBC36V30A complies with the following requirements:

EMC EN 61204-3

LVD

· EN60335-1/194 (Safety of household and similar electrical appliances-Part 1: General requirements); SIST EN 60335-1, May 1998; JUS IEC 60335-1 1998. and

· EN60335-2-29 (Part 2: Particular requirements for battery chargers); JUS IEC 60335-2-29 year 2000.

4. LCD Display

4.1. Setting mode

Setting mode can be entered only while the device is in READY mode (charge process has not been started). By turning R/S switch on the device turns into a setting mode and yellow led diode is on. In this mode buttons STOP and START take new meanings such as SCROLL and SELECT respectively. Navigation through menus is done by SCROLL button, by pressing SELECT one can enter submenu. If there are not sub-menus, than SCROLL acts like an increment of specific numeric values, and SELECT is used to confirm the set value. It is possible to reach desired specific value even faster by constant pressure onto SCROLL button. At any point it is possible to turn setting mode off and return to READY mode by simple click onto R/S switch when yellow LED diode turns off and the green turns on. All the previous done setting has been saved. 

4.2. Main screen (display)

The example of enlarged main screen:

	C
	H
	R
	
	9
	0
	.
	4
	A
	h
	
	5
	9
	.
	2
	V

	0
	4
	:
	3
	1
	:
	4
	9
	!
	3
	
	1
	0
	.
	0
	A


The first three characters in the first line of LCD display show the condition of device and they can be:

CHR
-marks charge operation,

FIN
-marks finished operation,

PA
-marks the condition of pause during alarm,

RDY
-marks ready condition after reset or at turning on the device. 

MAI
-marks battery maintenance operation after charging (poofer connection)

The following 7 characters are reserved for capacity display. Second line begins with a clock (altogether 8 characters for hours, minutes and seconds during charge process and 7 characters for minutes, seconds and tenths during discharge process). 

Ninth character of second line (such as exclamation mark) can be: 

SPACE
-marks process with factory values,

!

-Marks process with user defined values,

3

-marks current step in multi step charging

Second line finishes with current info. Blinking the alarm message on the main screen shows alarm conditions. 

4.3. The list of all the messages GBC36V30A is able to register while operating

	  G
	a
	u
	s
	B
	a
	t
	t
	.
	C
	h
	a
	r
	g
	e
	r

	
	G
	B
	C
	3
	6
	V
	3
	0
	A
	-
	A
	S
	-
	M
	S


It shows while turning the switch on if the device is plugged (Power ON).

	P
	O
	W
	E
	R
	
	F
	A
	I
	L
	U
	R
	E
	!
	
	

	p
	r
	o
	c
	e
	s
	
	c
	o
	n
	t
	i
	n
	u
	e
	d


Right after turning the device it’s been checked whether it had turned off by pressing OFF button or by power failure during charge process. If GBC detects this situation the previous charge process continues automatically with parameters as were set before.

	C
	h
	a
	r
	g
	e
	
	s
	t
	o
	p
	e
	d
	
	o
	n

	t
	i
	m
	e
	r
	
	c
	o
	u
	n
	t
	e
	r
	
	
	


If the user sets a new value to Charge Duration, after that charge process will be stopped (if it hasn’t been stopped for other condition or manually). Maintenance operation will automatically replace charge operation except in the case that user disabled maintenance operation in SET menu before he started charging*. 

	C
	h
	a
	r
	g
	e
	
	s
	t
	o
	p
	e
	d
	
	o
	n

	D
	e
	f
	a
	u
	l
	t
	
	t
	i
	m
	e
	r
	
	
	


If the user did not set new value to Charge Duration it would have a factory set value (96 hours). After that time charge process will be stopped* (if it had not been stopped earlier under any other condition or even manually).

	C
	h
	a
	r
	g
	e
	
	s
	t
	o
	p
	e
	d
	
	o
	n

	R
	e
	a
	c
	h
	e
	d
	
	c
	a
	p
	a
	c
	i
	t
	y


If the user set Capacity Limit (it had not been set in the factory), charge process would be stopped when the battery gets a certain amount of Ah. e.g. Capacity Limit = 200 Ah will stop charge* when the battery get 200Ah.

	C
	h
	a
	r
	g
	e
	
	s
	t
	o
	p
	e
	d
	
	b
	y

	U
	s
	e
	r
	
	
	
	
	
	
	
	
	
	
	
	


This message appears when the user manually stops charge process by pressing STOP button.

	V
	o
	l
	t
	a
	g
	e
	
	a
	l
	a
	r
	m
	!
	
	

	V
	o
	l
	t
	a
	g
	e
	
	
	>
	
	
	
	5
	4
	V


Alarm, when a higher voltage battery has been connected. Charge start is not possible! Also, if that situation happens during charging, GBC will stop.

	A
	l
	a
	r
	m
	
	N
	o
	
	b
	a
	t
	t
	e
	r
	y

	C
	h
	e
	c
	k
	
	c
	a
	b
	l
	e
	&
	f
	u
	s
	e


Alarm caused by a load disconnection, automatic fuse fail, and low battery voltage or cable disconnection. By turning the alarm off charge will automatically be continued.

	U
	s
	e
	r
	
	S
	e
	t
	t
	i
	n
	g
	s
	!
	
	

	P
	R
	E
	S
	S
	
	S
	T
	A
	R
	T
	
	
	
	
	


If charge process was started by user setting (not ones set by factory), this warning would inform him and would give him an opportunity to give up.

	T
	e
	m
	p
	e
	r
	a
	t
	.
	
	a
	l
	a
	r
	m
	

	h
	e
	a
	t
	s
	i
	n
	k
	
	t
	.
	
	>
	8
	0
	C


If the temperature of transistor heat sink is over 80C charge process will automatically be stopped. Start is not possible at this stage. The charge process will automatically be continued when the temperature falls under 50C unless the user resets the device earlier.

	T
	e
	m
	p
	e
	r
	a
	t
	.
	
	a
	l
	a
	r
	m
	

	A
	m
	b
	i
	e
	n
	t
	
	t
	.
	<
	
	
	
	5
	C


Ambient temperature is too low. Start is not possible. If charge were on it would be stopped until temperature exceeds 5C. Then it automatically continues unless the user hasn’t manually reset GBC.

	C
	h
	a
	r
	g
	e
	
	S
	t
	o
	p
	e
	d
	
	b
	y

	h
	i
	g
	h
	
	c
	u
	r
	r
	e
	n
	t
	
	
	
	


If current larger than 32A appear during charging, GBC will stop.

	C
	h
	a
	r
	g
	e
	
	S
	t
	o
	p
	e
	d
	
	b
	y

	l
	o
	w
	
	c
	u
	r
	r
	e
	n
	t
	
	
	
	
	


If charging current drops below 1A, GBC stops*.

*if maintenance operation is not set 
5. INSTRUCTION FOR USE

5.1. Device installation

1.
Turn the power supply socket on;

2.
Turn POWER switch on; 

3.
An intro message will appear on LCD display and will be on for 3 seconds. After this message the device will automatically continue charging process if it has already been on, or off by power fail or by a violent switching off. In that case another message, from the previous list, will be shown, charging process will be either continued or finished by pressing STOP button. If R/S switch is in READY position (green READY LED diode is on) MAIN SCREEN will be shown on LCD display and it is possible to read current battery voltage. If R/S switch is in SET mode (yellow LED diode is on), it should be turned into READY mode. At this level some settings could be made (that will be explained in the following text);

4. Connect charger loads onto the battery in a right way. Red load connects onto plus pole, and the black one onto a minus pole of the battery. PLEASE NOTE! Poles on the battery should be cleaned and a load properly fixed. Should be kept in mind to choose a connection for charge;

5. By pressing START button the device will ask you to select charging parameters such as charging voltage per cell (and complete battery) for constant voltage charging and current limit (see description below). Selection is made by SCROLL button (STOP button), and the set value is being confirmed by pressing SELECT (START button) once again, which starts charging process;

6. It is possible to follow charging process on LCD display (time that passed, charge current, charge voltage, inserted Ah capacity, the process status and eventually appeared irregular states caused by load disconnecting, warming-up etc.);

7. It is possible to stop the charging process at any time by pressing STOP button.

5.2. Starting charge


Pressing the button START in Ready State of device starts phase of setting charge parameters.

User Settings Press Start – this massage means that some settings which are different than default one are done by user in SET menu (symbol ! marks during charging that some parameters are set by user). Press Start button once again and select value of constant charge voltage and current limit.

Press on START/SELECT:

	C
	e
	l
	l
	
	V
	o
	l
	t
	.
	
	L
	i
	m
	i
	t

	2
	.
	4
	7
	V
	x
	6
	x
	
	4
	=
	
	5
	9
	.
	2


With button STOP/SCROLL choose voltage limit: 

Charge U/Cell:
2.47, 2.57, 2.67, 2.20....2.75 with step of 0.01V/Cell.

NOTICE: Voltage limit is very important for battery, which is charging and should be selected according battery manufacture’s instructions.  

Following description is not valid for multi step charging.  

Pressing on SELECT confirm selected value for charging voltage and opens window for setting charge current first with 10A step and after that with 1A step.

	
	S
	e
	l
	e
	c
	t
	
	C
	u
	r
	r
	e
	n
	t
	

	I
	s
	e
	l
	1
	0
	A
	s
	t
	e
	p
	:
	
	1
	0
	A


	
	S
	e
	l
	e
	c
	t
	
	C
	u
	r
	r
	e
	n
	t
	

	
	
	
	1
	A
	
	s
	t
	e
	p
	
	I
	=
	1
	5
	A


Pressing on SELECT confirm selected value for charging current and opens window for confirming charge parameters.

	U
	2
	.
	4
	7
	V
	/
	C
	
	I
	:
	
	
	1
	5
	A

	C
	o
	n
	t
	i
	n
	u
	e
	?
	
	
	
	
	Y
	e
	s


SCROLL changes Yes to No and vice verso. Press on SELECT starts charging (Yes) or cancel complete parameters setting procedure ( No).

Pressing STOP button at any time can stop charge.

In case of multi step charge, menu for setting current is skipped because current for each step is already set in SET menu during multi step settings. Continue massage is:

	U
	2
	.
	7
	5
	V
	/
	C
	
	
	
	1
	5
	5
	A
	h

	C
	o
	n
	t
	i
	n
	u
	e
	?
	
	
	
	
	Y
	e
	s


Display indicates amount of Ah according to chosen current and duration for each charging step in SET menu. 

6.  DEVICE SETTINGS

6.1. USER SETTINGS
Changing the switch READY/SET into SET position (yellow led diode turns on) enters the SET menu.

Press on SCROLL opens the first menu:

Default settings –for restoring original setting of charger.

	-
	-
	-
	-
	-
	m
	e
	n
	u
	
	1
	-
	-
	-
	-
	-

	D
	e
	f
	a
	u
	l
	t
	
	s
	e
	t
	t
	i
	n
	g
	S


Press on SELECT:

	D
	e
	f
	a
	u
	l
	t
	
	v
	a
	l
	u
	e
	s
	
	

	r
	e
	s
	t
	o
	r
	e
	d
	
	
	
	
	
	
	
	


Press on SCROLL:

Charge Condition – Group of charging conditions.

	-
	-
	-
	-
	-
	m
	e
	n
	u
	
	2
	-
	-
	-
	-
	-

	C
	h
	a
	r
	g
	e
	
	C
	o
	n
	d
	i
	t
	.
	>
	>


Press on SELECT:

Time Condition – Charging should be stopped after user defined time period (default – 96h).

Press on SCROLL:

	-
	-
	-
	-
	-
	m
	e
	n
	u
	
	2
	a
	-
	-
	-
	-

	T
	i
	m
	e
	
	C
	o
	n
	d
	i
	t
	i
	o
	n
	>
	>


Press on SELECT:

	-
	-
	-
	S
	T
	O
	P
	
	a
	f
	t
	e
	r
	-
	-
	-

	
	9
	6
	
	H
	r
	s
	
	:
	
	
	
	
	m
	i
	n


By combining buttons SCROLL and SELECT it is possible to set up charge duration from 15 min to 96h (steps 1h and 15 min).

	-
	-
	-
	S
	T
	O
	P
	
	a
	f
	t
	e
	r
	-
	-
	-

	
	1
	0
	
	H
	r
	s
	
	:
	
	3
	0
	
	m
	i
	n


During start procedure display appears as:

	T
	:
	1
	0
	h
	3
	0
	m
	C
	:
	
	1
	5
	7
	A
	h

	I
	s
	e
	l
	1
	A
	s
	t
	e
	p
	:
	
	
	1
	5
	A


After selecting charge duration, user can set up amount of Ah in charge process:

Capacity Condition.

	-
	-
	-
	-
	-
	m
	e
	n
	u
	
	2
	b
	-
	-
	-
	-

	C
	a
	p
	a
	c
	i
	t
	y
	
	C
	o
	n
	d
	.
	>
	>


Press on SELECT opens capacity condition menu:

	-
	-
	-
	S
	T
	O
	P
	
	a
	f
	t
	e
	r
	-
	-
	-

	
	
	0
	
	A
	h
	
	L
	o
	a
	d
	e
	d
	
	
	


Amount of Ah in charge process is choosing by combining SCROLL and SELECT buttons.

Following menu is for choosing maintenance operation which will (or not) automatically start after finishing regular charging (for poofer connection, keeping battery always ready).

	-
	-
	-
	-
	-
	m
	e
	n
	u
	
	2
	d
	-
	-
	-
	-

	m
	a
	i
	n
	t
	e
	n
	a
	n
	c
	e
	
	
	
	>
	>


Press on SELECT opens menu with YES/NO options.

	I
	n
	c
	l
	u
	d
	e
	
	B
	a
	t
	t
	e
	r
	y
	

	m
	a
	i
	n
	t
	e
	n
	a
	n
	c
	e
	?
	
	Y
	e
	s


After confirming selection, SCROLL button opens submenu, which permit return to menu 2.

	-
	-
	-
	-
	-
	m
	e
	n
	u
	
	2
	e
	-
	-
	-
	-

	<
	<
	
	B
	a
	c
	k
	
	
	
	
	
	
	
	
	


Press on SCROLL in root shows menu 3 for selecting number of batteries for charging in serial connection.  

	-
	-
	-
	-
	-
	m
	e
	n
	u
	
	3
	-
	-
	-
	-
	-

	S
	e
	l
	.
	N
	o
	.
	B
	a
	t
	t
	e
	r
	i
	e
	s


In this menu it is possible to select No 12V batteries from 1 to 4.
	S
	e
	l
	e
	c
	t
	
	N
	u
	m
	b
	e
	r
	
	o
	f

	1
	2
	V
	
	B
	a
	t
	t
	e
	r
	i
	e
	s
	:
	
	3


By pressing SCROLL in root, Multi-step menu appears.

	-
	-
	-
	-
	-
	m
	e
	n
	u
	
	4
	-
	-
	-
	-
	-

	M
	u
	l
	t
	i
	S
	t
	e
	p
	P
	r
	o
	g
	.
	>
	>


Press on SELECT, opens menu with question for enabling multi step charging.

	D
	e
	f
	i
	n
	e
	M
	u
	l
	t
	i
	S
	t
	e
	p
	

	P
	r
	o
	g
	r
	a
	m
	:
	
	
	
	
	
	Y
	e
	s


In case of enabling multi step, next step is to define number of charging steps (from 2 to 4).

	D
	e
	f
	i
	n
	e
	
	N
	u
	m
	b
	e
	r
	
	o
	f

	P
	r
	o
	g
	r
	a
	m
	
	S
	t
	e
	p
	s
	:
	
	4


After that, it is necessary to define current and duration for each step.

	I
	
	&
	
	d
	T
	
	s
	t
	e
	p
	:
	
	
	
	3

	I
	:
	
	3
	.
	0
	A
	
	d
	T
	:
	1
	0
	.
	5
	h


For each step (in this example the third one) current should be chosen from 0A to 50A with 1A step and duration from 0 to 24h with 0,5h step. Selecting step current as 0A means operation of Pausing (step or period of time without current). If duration for step is chosen as 0, that step will be ignored.

Also, with SCROLL in root, it is possible to open menu with information about number of power failure situations during last charge process.

Power Fail last process 

	-
	-
	-
	P
	o
	w
	e
	r
	
	F
	a
	i
	l
	-
	-
	-

	L
	a
	s
	t
	
	p
	r
	o
	c
	e
	s
	s
	:
	
	
	0


Notice: All settings in SET option menus, remains in device memory only until it’s shut off. Original setting is restored on next turn on. Warning USER SETTINGS follows starting charging with parameters different than original ones!

7. LEGEND OF MARKS (SIGNS) AND CONCEPTS

A-(Amper) current unit 

V- (Volt) voltage unit 

Capacity Ah – battery capacity unit 

Charge (CHR) – Charge

Maintenance (MAI) – Maintenance operation

Set – Setting of parameters

Ready (RDY) – Ready for work (start)

Start – Starting process

Stop – Stopping process

Current – value of DC current

Buzzer – part for sound beeping

LCD Display – Display with 2x16 characters

Password – for skilled users

Voltage limit – value of charging voltage on which some action has to be done

Power failure – Main power supply failure

Finish (FIN) – Finishing operation

Pause (PA) – Freezing operation 

Alarm voltage limit – unacceptable voltage level

Alarm current – unacceptable current level

Time Condition – time condition for charge ending

Capacity Condition – capacity condition for charge ending

Default settings for Gaus Battery Charger GBC36V30A

	Parameter
	Range
	Default

	Charge Voltage/Cell
	2.20V/Cell – 2.75V/Cell

settable by user from START menu with 0.01V/Cell step
	2.47V/Cellx6x3= 44.4V

internally set

	Number of 12V Batteries in serial connection
	1-3
settable by user from SET menu
	3 (36V)

internally set

	Charge Current
	0A-30A, settable by user from START menu with 1A step
	30A

internally set

	Alarm Low Voltage
	-
	5V

internally set

	Alarm High Voltage
	-
	54V

internally set

	Alarm Current 
	-
	32A

internally set

	Minimum Current (Current stop)
	-
	0.175A

0A if Iselect=0A PAUSE

internally set

	Capacity Condition
	0-405Ah 

0Ah means that capacity condition should be ignored , settable by user from SET menu with 5Ah step
	not defined, 0Ah

	Time Condition
	1min-96h 45min

settable by user from SET menu, 15min step
	96h:00min

	Maintenance (poofer connection) operation*
	Yes/No

choosing by user from SET menu
	Yes

	Charging parameters in maintenance operation
	Charging with constant voltage at 2.25V/Cell * No. Cell (24 for 48V batt.)
current limit is the same one which was chosen through START menu by user
	

	MultiStep
	No/Yes choosing from SET menu
	No

	NoSteps in MultiStep
	2-4, settable from SET menu
	2


*If Maintenance operation is included in charging process, that means that after regular charging with chosen voltage and current limit, charger will automatically continue with charging the battery with constant voltage of 2.25V/Cell * No. Cell (poofer connection). In that case, charging can be stop only manually by pressing STOP taster. In case of power failure, charger continues after its restoring. 

Also, time and capacity conditions, default timer condition are ignored in maintenance operation.

If user use multi step charging, maintenance operation will follow charging in steps, unless user in SET menu disables that operation before starting charge process. 

9. PRECAUTION MEASURES

1. Please read the instruction for use and warnings;

2. To avoid electric shock, disconnect the cable and test cables from the battery before taking the device cover off or before safety fuse change;

3. WARNING! Gases realised during charge process are explosive. Do not smoke, avoid fire and sparkles;

4. Do not expose device to direct sun light, extreme temperature or moisture;

5. Device must be earth grounded;

6. Do not connect device to battery with nominal voltage larger than 36V. Connected battery voltage must be ranged 5 to 50 volts;

7. Do not connect the device on a battery that is in a vehicle. Charged or tested battery should be outside any vehicle;

8. Always take into consideration the correct polarity while connecting the battery. Red cable onto plus, black onto minus battery pole. Inversion polarity is situation in which it is not possible to start charging;

9. Place the device to enable right flow of dissipated heat (do not cover ventilation holes). Use the device only in well ventilated areas. Avoid intensive warming and battery «boiling» during charge;

10. Keep the device away from children;

11. Only skilled and qualified person can service the device.







13
10
GAUS StS-Belgrade, Jurija Gagarina 167/41, tel/fax: +381 11 22 79 142, mob. +381 63 215 722, serv. +381 25 421 095

www.gaus-sts.com, gaus.sts@eunet.rs, nelija1@open.telekom.rs, gaus.sts@sbb.rs, gaus.sts@gmail.com 

