GSBCT25A12V Software
[image: image1.png]Visit our site

Command Realtine DB Results Settings

‘GAUS STARTER BATTERY CAPACITY TESTER GSBCT25A12Y

@ o AdjustRTC DatefTime.
Clear All Results in FLASH





Figure 1.

[image: image2.png]Command

Realtime. DB Results

Settings

Copactyno

Tine i)
Test Tine [Himin] | Ve V] Curent 4] Capaciy ()
BEFORE START 6570 om0 om0
0h00m 6450 3820 oo
OhOim 6270 4000 087
Oh02m 6270 3980 1.34
6270 4000 201

Oh0Im





Figure 2.

[image: image3.png]9 Soloct Desired Values

Current [A]:
]

100.00

Voltage ICell [V]: 175
[

Number of cells
“6 12
24 - 30

Final Voltage [V]: 10.50

Time: 40 h: 0 min
T

Discharge Capacity [Ah]:

4000.0





Figure 3.
[image: image4.png]Current test parameters

Desired cunent: 50 A

Break voltage per cell 1.75 v/

Number of cels: &

Break voltage: 0.6V

Test duration 40 h 0 min

Discharge capacity: 2000.0 Ah Close




Figure 4.

After Typical installation of software from installation CD, registration is necessary (New user) using data from license. Password is user settable. Device is connected with PC if  Connected  (white letters Figure 2.) is indicated on the bottom of the screen. Connection doesn't exist if red Inactive (Figure 1.) is on the screen. It is necessary to adjust in device manager that serial RS232 port is COM1 or COM2 because in GSBCT Software in Settings screen 
only these two options are present. If you are using USB-RS232 adapter it has to be set as COM1 or COM2 on PC (device settings...). 
If device (GSBCT) is connected, than on screen Command you can read test results from devices memory Read results from FLASH. You can save results in database (Figure 1.).
Using Adjust RTC Date/Time you can change date and time in GSBCT.
Clear All Results erase GSBCT memory.
On screen Real Time (Figure 2.) you can turn on monitoring of test current and battery voltage, you can start test in real time, monitor it, stop it, set Set Parameters (Figure 3.) and view test parameters View Parameters  (Figure 4.). 
[image: image5.png]Visit our site

Command Realtine

Tine Current Voage

Copactyno

Tirne [min

0 10 20 30 40 50 B0 70 80 90 100 110 120 130 140 150 160 170 180 190 200 210 220 230 240 250 260 270 260 290 300 310 320 330 340 350

omment
TESTNAME [Dae |Time |Succ |DesiedVok./C... |Desied Curend 4] D
v/ Group! 4032012_0012
[ [resm 5032012 #1825PM Fal B3 | I
TEST2 15032012 50838 PM _Fal 175 1000
bl PARS_TEST? 0w s 2 000)
b/ PRODTT_1402012 oo wm _2x 0%
b/ PRODTT_2 o wm _2x 07
b/ PRODT2_ 14032012 0om  wn _2x 709
»| PROEV10A_26012012 00 mm 2x 746
b/ RealTime Grous 0% mm o .83
b/ US2200 8RS 0% mm 20 219
> b 0w wn 20 255
v/ US2200_ PARS3 0 mm 20 29|
0w  wm  2x 39|
0l mm 20 386]
. N 0N wm 2x )

Realtime test started





Figure 5.
Tests are stored in Database (Figure 5.) screen DB Results. There are two test types, tests which are done in real time with PC and GSBCT Software and tests which are from flash memory of GSBCT.
It has a table display of current, voltage, capacity for each moment of registration of the test (1min or 4min), current, voltage and capacity chart, with the possibility to include Show Marks for each point registered in time. It's possible to zoom in/out on a graph (clicking on a mouse...), 2D or 3D display, rotation, etc. ...
The table with the name of the test is editable and it is possible to manually enter some data that will be stored along with the results and test parameters that are not editable (variable).
The selected test from the database is transmitted to the Results panel to produce the report (Figure 6).
On the Results Panel it is also possible to display some previously processed test by dragging the PDF file from the directory that the user created for this purpose.
The report can be header in Serbian or English.
In the space provided for data entry it is possible to enter data on the service (test center), the client, the battery, the comments on the reception, after test done, the density of electrolytes per cell ...
Before printing, the test should be saved in PDF format (Figure 7) in the directory that the user provides for it. The testname.pdf is manually added to the test name
The printed report is shown in Figures 8, 9 and 10.
[image: image6.png]English

Service:
Place:
Address:
TelFa:

Client
Place:
Address:
TelFa:

Notie:

Battery:
Marutacturer
Seral rumber.
Assemblng date:
Seling date:

Comment:

Cells [g/cm3]

Opservation:

e

BATTERY CAPACITY TEST REPORT

[GAUS5.1.5. dos Radiorica Sambor

[25000 Sambor

[Vere Gucurie 13

[-381 25 421 035, 063 215 722

[WL COMUNICATIONS doo

[Beogiad

[Viadmia Miovica 15

Continue >>>




Figure 6.
[image: image7.png]Output Options

Selected Priner
USASKAIVANAHP Laserdet Professional P1102w_

Report Destination

Options.

Copies.

=





Figure 7.

[image: image8.png]Fie Page Zoom

Sl @ » >l Page |1 ofd | & A m B zoom [ % B

Opservation:

Comment
Operater:

BATTERY CAPACITY TEST REPORT

Service: GAUS-5.T.5. doo Radionica Sombor Place: 25000 Sombor
Address; Vere Gucunje 13 TedFax 438125 421095, 063 215 722
Client: AWL COMUNICATIONS doo Piace: Beograd
Address; Vladirira Mitrovica 15 TelFax
Notice:
Battery: Manufacturer Serial number
Assembling dete: Selling dete:
Cells: [giem3] 126 1275
127 127
27 27
27 27
Cormment:
Test results: Testing device: Gaus PRABYI00A
Test parameters:
Test No TESTI Test date: 25022009 Test time: 12:32:33 PM
Test cunent (A} 20 Break U/Cell [V} 175 Test duration [m: 48h 00m
Test resul Fail

MP.





Figure 8.
[image: image9.png]Fie Page Zoom

ad$ » >l page [1 ofd | & & = B Zoom [IE % | B

Test No TESTI Test date: 25022009 Test time 123233 PM
Test cunent (A} 20 Break U/Cell [V} 175 Test duration [m: 48h 00m
Test result: Fail

Opservation:

Comment:
Operater: MP.

Printing date: 09.09.2015 1:13 PM

EP

L U WAWARER ORI AR R

i i)

Time[humin] Voitage[V] Current[A] CapacityAh] Time{htmin] Voltage[V] CurrentA] Capacity{Ah]

wa cpnm

Before Start  S1.70 0.00 0.00 0:00  4s.60  -2L.20 0.00
00l 4330 -zz.20 035 00z as3  -zz.20 072

»





Figure 9.

[image: image10.png]= Report Preview

Fie Page Zoom

SHE 4 Page [+ of4 | & & = B Zoom [ % | B

Time[humin] Voitage[V] CurrentA] Capacitylh] Time{htmin] Voltage[V] CurrentA] CapacityAh]
4:47  45.10  -22.00  -104.33 4 45.10 -2z.20  -104.69
4:49 4510 -22.00  -105.06 a: 45.00  -2z.20  -105.43
4:5L 45,00  -22.00  -105.80 4 45,00 -zz.00  -106.17
4:53  45.00 -22.00  -106.53 4 44.90  -2z.00  -106.90
4:55  4aale0  -zz.00  -107.27 4:5 4490 -22.00  -107.63
4:57 4480 -22.00  -108.00 4:58  aas0  -22.00  -108.37
4:59 4480  -22.00  -108.73 5:00 4470 -22.00  -109.10
5:0L 4470  -zl.e0  -109.47 5:02 4470 -22.00  -109.83
5:03 4470  -z2.00  -110.20 5:04 4470 -zl.e0  -110.56
5:05 4470  -zl.eo  -110.93 5:06  aa60  -z2.00  -111.29
5:07 4460 -zl.e0  -111.66 5:08  aasp -zz.00  -11z.02
5:09 4450 -zl.eo  -112.39 5:l0  aasp  -zl.eo  -112.75
5:ll 44040 -zlieo -113.11 5:lz  adan  -zlieo  -113.48
5:13 4440 -2l.80  -ll3.e4 5:14  ada0  -zl.e0  -114.20
5:15 4430  -2l.e0  -114.57 5:l6 4430  -zl.e0  -114.93
5:17 4430  -zlieo -115.29 5:ls  ad20  -zl.e0  -115.65
5:ls 4420 -zl.60  -116.01 5:20  ad2n  -zl.e0 -116.37
5i2l 440 -zlie0 -116.73 5i22  aalo  -zlieo -117.09
5:23 4410 -2l.60  -117.45 5:24  aalo  -zl.e0 -117.81
5:25 4400  -zl.e0  -118.17 5:26  a4so0  -2l40 -118.53
5:27 430 -zz.60  -118.89 5i28  anen  -z2.40  -119.27
5:29 4370  -z2.60  -119.64 5:30  an70 22040 -120.02
5:3 4370 22040 -120.39 5:32  anen  -z2.40  -120.76
5:33 4360 -22.40  -l2L.14 5:34  ane0  -2l.40 -12L.51
5:35 4350 -zz.20  -lzlet 5:3  a4ns0  -zz.20  -lzz.2d4
5:37 43S0 -2la0 -lzz.el 5:3  anap  -2li20 -122.96 5
5:3 4340  -2l.40 -123.32 5:40  anap  -2l20 -123.67
5:al 4330 -2li20 -124.03 542 aslo 2220 -124.38
5:43 4310 -22.20  -124.75 5:44  anlo -zloo -125.12
5:45 4300  -22.00  -125.47 5:45 a4z -zz.00  -lzs.ad
5:47  4zie0  -zz.00  -126.20 5:48 az.eo -zl.e0  -126.57
5:49 4270 -22.00  -126.93 5:50 4270 -z2.00  -127.30
5i5L 4z0  -z2.00  -127.67 5:52  az.sn 22,00 -128.03
5:53  4z.50 -zl.e0  -128.40 5:54  az.ap  -zl.e0  -128.76
5:55 4230  -2l.e0 -129.13 5:56  a4z.30  -zl.e0  -129.49
5:57 4220 -2l.e0  -129.85 5is8  azlo -zl.eo -130.21
5:59 4200 -2l.60  -130.57

Page 4 of 4




Figure 10.

PAGE  
1
GAUS StS-Belgrade, Jurija Gagarina 167/41, tel/fax: +381 11 22 79 142, mob. +381 63 215 722, serv. +381 25 421 095

www.gaus-sts.com, gaus.sts@eunet.rs, nelija1@open.telekom.rs, gaus.sts@sbb.rs, gaus.sts@gmail.com

